BOILER TECHNICAL GRAM
Number:      2012-01
Date:
January 11, 2012
To:
Authorized Inspectors


Authorized Inspection Agencies

From:
Office of the Chief Inspector


TDLR, Compliance Division, Boiler Program

Subj:
Boiler Technical Grams

Re:    ASME Section I Boiler Safety Valve Changeover Valve
Ref:  Texas Boiler Law and Rules:  65.100 (g) (1) Safety valves and safety relief valves 

The reference rule prohibits any valve from being installed between the boiler and the safety valve(s) or safety relief valve(s).  After observing the actual operation of the Tyco Valves & Controls Safety Selector Valve and reviewing Texas Boiler Law and Rules, ASME Code Case 2254, and the valve specifications, we have determined that the changeover valve meets the Code case criteria, addresses the safety requirements of the Texas Boiler Law and Rules, and that equivalent safety will be maintained with this variation.   Since the installation of this valve is a direct violation of 65.100 (g) (1), a Repair Requirement Form and Variance Request is still required until the Rule may be modified.
The attached literature clearly shows that neither mounted safety valve can be isolated at any time, even while changing over from one safety valve to the other.  The 2011 NBIC Part 1, para 2.9.6 (D) was also revised to incorporate changeover valves.  

This ‘Safety Selector Valve’ may now be installed between the boiler and the safety valve on ASME Section I boilers in Texas provided it meets the pressure/temperature design of the boiler and the owner/user applies for and obtains a variance.  The remaining mounting requirements of Section I PG-71 still apply and the valve will be locked when not in operation.  Should other manufacturers design and produce a changeover valve that meets the ASME Code case requirements, the specifications will be reviewed by this office prior to being approved for installation.
Any questions regarding this Technical Gram should be addressed to the Chief Inspector or an Inspection Specialist.

