
BOILER TECHNICAL GRAM

Date:
August 31, 2011
To:
Authorized Inspectors

Authorized Inspection Agencies
From:
Office of the Chief Inspector

TDLR, Compliance Division, Boiler Program
Subj:
Boiler Technical Grams

Re:   Noritz Tankless Water Heater LWFC Devices
Ref:  Texas Boiler Law and Rules: 65.100 (k) (4) (c) (i)

A LWCO is not required on a Potable Water Heater per the Texas Boiler Law and Rules; however, a flow sensing device is required when the water heater is of a coil-type or a water-tube boiler requiring “forced circulation”.

We have seen numerous Boiler Inspections Reports on Noritz water heaters with no data documented in the LWFC Type and LWFC MAWP block on page 2.  Because these heaters require forced circulation, Noritz has installed two “flow sensors” (Exhibit 1) into their boilers, thus meeting the requirement of the rule quoted above.  The flow sensing device which Noritz calls a “flow sensor” is a flow switch and has a rating of 156 psi. This information shall be included on all “First Inspection Reports” and “Subsequent Inspection Reports” in the LWCO MAWP and Type blocks for this boiler.
Any questions regarding this Technical Gram should be addressed to the Chief Boiler Inspector or an Inspection Specialist.

Exhibit 1
[image: image1.emf]
Main Flow Sensor                                Bypass Flow Sensor

Flow must be maintained through the Main and Bypass Flow Sensors in order for burners to be active











