BOILER TECHNICAL GRAM
Date:
February 8, 2007
To:
Authorized Inspectors

Authorized Inspection Agencies

From:
Office of the Chief Inspector


TDLR, Compliance Division, Boiler Program

Subj:
Takagi MOBIUS T-M1 Instantaneous Water Heater
This particular model of Takagi is rated for:

235,000 Btu/hr NG

225,000 Btu/hr LPG

The factory has a procedure to derate the input to less than 200,000 Btu/hr.

This procedure will only be allowed if all of the following are completed:

1)
the procedure is done by a Takagi Factory Technician per their T-M1 “manifold adjustment procedures”; and

2)
the original manufacturer’s rating plate on the front panel is removed and a new plate installed showing input rating of less than 200,000 Btu/hr.

If these adjustments are not made, the boiler is considered non-Code and must be replaced with a Code item.

Upon finding these boilers, register them with a First Inspection as normal.  Write a Repair Requirement to derate boiler and on any other repairs.  After the boiler has been verified “derated”, the boiler will be “removed from active status” and the Repair Requirement cleared as such.

Any questions regarding this Technical Gram should be addressed to Terry Parks, Chief Inspector, George Solomon, Don Evitt or Anthony Jones, Inspection Specialists.

